## ACI 318-19
ACI 318-19 — Formulas Used in This Workbook (Chapters 19–22) |  |  |  | Table 19.2.4.1(a)—Values of landa for lightweight concrete based on equilibrium density | Table 19.2.4.1(b)—Values of 􀈜 for lightweight concrete based on composition of aggregates
Check / Term | ACI 318-19 Ref. | Formula (as implemented) | Notes / Units
Concrete lightweight factor, λ | 19.2.4.1 / Table 19.2.4.1(a) | λ = 1.0 (wc>135 pcf); λ = 0.75 (wc≤100 pcf); else λ = min(1.0, 0.0075·wc) | wc = equilibrium density (pcf)
Steel modulus, Es | 20.2.2.2 | Es = 29,000,000 psi | Nonprestressed bars & wires
Yield strain, εty | 21.2.2.1 | εty = fy/Es | Grade 60 permitted εty=0.002
Strength reduction factor (shear) | Table 21.2.1 | ϕv = 0.75 | Used for one-way & punching shear
Strength reduction factor (bearing) | Table 21.2.1 | ϕb = 0.65 | Used for concrete bearing
Strength reduction factor (flexure) | Table 21.2.2 | For ‘Other’: ϕ=0.65 if εt≤εty; ϕ=0.90 if εt≥εty+0.003; else ϕ=0.65+0.25·(εt−εty)/0.003 | Workbook computes εt at nominal strength
Concrete max compressive strain | 22.2.2.1 | εcu = 0.003 | Used in εt calculation
Stress block depth | 22.2.2.4.1 | a = β1·c | Equivalent rectangular stress block
β1 factor | Table 22.2.2.4.3 | β1 = 0.85 (fc'≤4000 psi); else β1 = max(0.65, 0.85 − 0.05·(fc'−4000)/1000) | Inch-pound units
Compression block force | 22.2.2.4.1 | C = 0.85·fc'·a·b | Used implicitly through a-expression
Flexural nominal strength (singly reinforced) | 22.2 assumptions + equilibrium | Mn = As·fy·(d − a/2) | Assumes steel yields; check via εt
One-way shear size effect factor | 22.5.5.1.3 | λs = min(1, 2/(1 + d/10)) | d in inches
One-way shear strength by concrete (no shear reinforcement) | Table 22.5.5.1(c) | Vc = [8·λs·λ·ρw^(1/3)·√fc' + Nu/(6Ag)]·bw·d; Vc ≥ 0 | Nu positive compression; ρw=As/(bw·d)
Two-way shear stress by concrete (no shear reinforcement) | Table 22.6.5.2 | vc = least of: (a) 4·λs·λ·√fc' ; (b) (2+4/β)·λs·λ·√fc' ; (c) (2+αs·d/b0)·λs·λ·√fc' | Vc = vc·b0·d
αs for punching | 22.6.5.3 | αs = 40 interior; 30 edge; 20 corner | User selects location
Bearing strength check | 22.8.3.1 | ϕ·Bn ≥ Bu | Bu factored compressive force
Nominal bearing strength | Table 22.8.3.2 | If support wider on all sides: Bn = min(0.85·fc'·A1·√(A2/A1), 2·0.85·fc'·A1); otherwise Bn=0.85·fc'·A1 | A2 from 1V:2H frustum within support

## Wind and Seismic
wind load paramets | [11 empty] | seismic base shear
kzt | 1 | [10 empty] | Ss | 0.346 | g
kd | 1 | [10 empty] | S1 | 0.15 | g
I | 1 | [10 empty] | SDS | 0.36907 | g
V | 116 | mph | Number of Columns | 4 | [7 empty] | SD1 | 0.24 | g
exposure | D | [10 empty] | Ri | 3
α | 11.5 | [10 empty] | IE | 1.5
Zg | 700 | ft | [9 empty] | TL | 12 | sec
G | 1 | [10 empty] | Ti | 1.5511 | sec
Cf | 0.7 | [10 empty] | Ts | 0.65029 | sec
λ | 0.6 | [10 empty] | Sai | 0.15473
λ(0.00256 Kzt Kd I V2) | 20.6684 | psf | [9 empty] | λ | 0.7
column |  |  | column |  |  | column |  |  | column |  |  | Ai | 0.054155 | ft/s2
Bay Number | 1 |  | Bay Number | 2 |  | Bay Number | 3 |  | Bay Number | 4 |  | COM | 108.4665
Thickness | 0.3125 | in | Thickness | 0.3125 | in | Thickness | 0.25 | in | Thickness | 0 | in | V | 52.2954 | kips
hi | 0 | ft | hi | 38.0544 |  | hi | 73.1674 | ft | hi | 0 | ft | Seismic base moment | 5672.3022 | kips-ft
Height of the cylinder | 38.0544 | ft | Height of the cylinder | 35.113 | ft | Height of the cylinder | 35.1488 | ft | Height of the cylinder | 0 | ft
hf | 38.0544 | ft | hf | 73.1674 |  | hf | 108.3162 | ft | hf | 0 | ft
Diameter of the cylinder | 1.67 | ft | Diameter of the cylinder | 1.67 | ft | Diameter of the cylinder | 1.67 | ft | Diameter of the cylinder | 0 | ft
Awind | 254.2034 | ft2 | Awind | 234.5548 | ft2 | Awind | 234.794 | ft2 | Awind | 0 | ft2
Centroid | 19.0272 | ft | Centroid | 55.6109 | ft | Centroid | 90.7418 | ft | Centroid | 0 | ft
kzi | 1.0302 |  | kzi | 1.2113 |  | kzi | 1.3571 |  | kzi | 1.0302
kzf | 1.2113 |  | kzf | 1.3571 |  | kzf | 1.453 |  | kzf | 1.0302
qzi | 21.2932 | psf | qzi | 25.0355 | psf | qzi | 28.05 | psf | qzi | 21.2932 | psf
qzf | 25.0355 | psf | qzf | 28.05 | psf | qzf | 30.0306 | psf | qzf | 21.2932 | psf
F | 5.3383 | kips | F | 4.9257 | kips | F | 4.9307 | kips | F | 0 | kips | Wind base shear | 15.1946 | kips
F location | 19.5395 | ft | F location | 55.9432 | ft | F location | 90.9416 | ft | F location | 0 | ft
Wind moment At base | 104.3073 | kips | Wind moment At base | 275.5568 | kips | Wind moment At base | 448.4032 | kips | Wind moment At base | 0 | kips | Wind base moment | 828.2672 | kips-ft
Center of mass x weight | 222.104 |  | Center of mass x weight | 685.6258 |  | Center of mass x weight | 953.585 |  | Center of mass x weight | 0
Weight | 11.673 | kips | Weight | 12.329 | kips | Weight | 10.5088 | kips | Weight | 0 | kips | weight of steel | 34.5107 | kips
riser |  |  | riser |  |  | riser |  |  | riser
Bay Number | 1 |  | Bay Number | 2 |  | Bay Number | 3 |  | Bay Number | 4
Thickness | 0.3125 | in | Thickness | 0.3125 | in | Thickness | 0.3125 | in | Thickness | 0 | in
hi | 0 | ft | hi | 38.0544 |  | hi | 73.1674 | ft | hi | 0 | ft
Height of the riser | 38.0544 | ft | Height of the riser | 35.113 | ft | Height of the riser | 25.4993 | ft | Height of the riser | 0 | ft
hf | 38.0544 | ft | hf | 73.1674 |  | hf | 98.6667 | ft | hf | 0 | ft
Diameter of the riser | 3 | ft | Diameter of the riser | 3 | ft | Diameter of the riser | 3 | ft | Diameter of the riser | 0 | ft
Awind | 114.1632 | ft2 | Awind | 105.339 | ft2 | Awind | 76.4979 | ft2 | Awind | 0 | ft2
Centroid | 19.0272 | ft | Centroid | 55.6109 | ft | Centroid | 85.9171 | ft | Centroid | 0 | ft
kzi | 1.0302 |  | kzi | 1.2113 |  | kzi | 1.3571 |  | kzi | 1.0302
kzf | 1.2113 |  | kzf | 1.3571 |  | kzf | 1.4296 |  | kzf | 1.0302
qzi | 21.2932 | psf | qzi | 25.0355 | psf | qzi | 28.05 | psf | qzi | 21.2932 | psf
qzf | 25.0355 | psf | qzf | 28.05 | psf | qzf | 29.5472 | psf | qzf | 21.2932 | psf
F | 2.3974 | kips | F | 2.2121 | kips | F | 1.6065 | kips | F | 0 | kips | Wind base shear | 6.216 | kips
F location | 19.5395 | ft | F location | 55.9432 | ft | F location | 86.0275 | ft | F location | 0 | ft
Wind moment At base | 46.8446 | kips | Wind moment At base | 123.7531 | kips | Wind moment At base | 138.1994 | kips | Wind moment At base | 0 | kips | Wind base moment | 308.7971 | kips-ft
Center of mass x weight | 86.3236 |  | Center of mass x weight | 232.797 |  | Center of mass x weight | 261.1904 |  | Center of mass x weight | 0
Weight | 4.5369 | kips | Weight | 4.1862 | kips | Weight | 3.04 | kips | Weight | 0 | kips | weight of steel | 11.7631 | kips
Water tank properties | [5 empty] | other parts' weight on columns |  |  | other parts' weight on riser
Tank type | 100K-DE | Gal. |  |  |  | struts | 2.8628 | kips | weight of bowl | 0 | kips
hi | 98.67 | ft
hf | 123.8856 | ft |  |  |  | cross bracing | 4.9241 | kips | upper cone | 0 | kips
kzi | 1.4296
kzf | 1.4873
qzi | 29.5473 | Psf
qzf | 30.7402 | Psf
F | 12.9136 | Kips
Centroied | 111.27 | ft
tank height | 25.2156 | ft
Weight of water | 879 | Kips
Weight of steel | 40.3865 | Kips
Total weight | 919.3865 | Kips
projected area | 612 | ft2
Wind shear | 12.9136 | Kips |  |  |  | SUM | 7.7869 | KIPS | SUM | 0 | KIPS
weight of water | 879 | kips
weight of steel | 86.6603 | kips
Total weight | 965.6603 | kips
Totals reactions
Wind base shear | 34.3242 | kips
Wind base moment | 2573.9605 | kips-ft

## Loads
Snow Load |  |  | Roof Live Load |  |  | Live Load |  |  | Load Combination | P | M
Diameter of tank | 32 | ft | Min Roof Live Load | 15 | psf | Live Load | 0 | kips | D | 965.6603 | 0
Height to consider | 6.6437 |  | Area to consider | 667.8976 | ft2 |  |  |  | D + L | 965.6603 | 0
Area to consider | 667.8976 | ft2 | Roof Live Load | 10.0185 | kips |  |  |  | D + (Lr or S) | 979.1251 | 0
Ground snow load | 25 | psf | [6 empty] | D + 0.75L + 0.75(Lr or S) | 975.7589 | 0
Exposure Factor | D | [7 empty] | D + 0.6(W or E) | 965.6603 | 3403.3813
Ce | 0.8 | [7 empty] | D + 0.75L + 0.75(0.6W or 0.6E) + 0.75(Lr or S) | 975.7589 | 2552.536
Ct | 1.2 | [7 empty] | 0.6D + 0.6(W or E) | 579.3962 | 3403.3813
Importance Factor | RC IV
Is | 1.2
Snow load | 13.4648 | kips
0.6D + 0.6(W or E) |  |  | D + 0.75L + 0.75(0.6W or 0.6E) + 0.75(Lr or S) |  |  | D + 0.6(W or E)
579.3962 | kips |  | 975.7589 | kips |  | 965.6603 |  | kips
3403.3813 | ft-kips |  | 2552.536 | ft-kips |  | 3403.3813 |  | ft-kips

## Inputs
Water Tank Foundation Design (ACI 318-19)
Project / References
Project | Ute, IA – 100,000 gal Pedesphere
Design Standard | ACI 318-19 (Strength design)
Units | US Customary (in, ft, kip, psi)
Material Properties
Concrete compressive strength, f'c (psi) |  | 4000
Rebar yield strength, fy (psi) |  | 60000
Concrete unit weight (pcf) |  | 150
Steel unit weight (pcf) |  | 490
Phi factors (ACI 318-19) |  | Shear: 0.75 (Table 21.2.1), Bearing: 0.65 (Table 21.2.1), Flexure: per Table 21.2.2
Steel modulus, Es (psi) |  | 29000000 | ACI 318-19 20.2.2.2
Lightweight factor, λ (auto) (19.2.4) |  | 1 | Table 19.2.4.1(a)
Geotechnical Inputs
Allowable soil bearing, q_allow (psf) |  | 4000
Soil unit weight, γ_s (pcf) |  | 120
Frost depth (ft) |  | 4
Base friction coefficient μ (if needed) |  | 0.5
Soil-to-footing contact condition |  | Uniform bearing assumed (service level)
Loads (enter best-available values)
Water volume (gal) |  | 10000
Water unit weight (pcf) |  | 62.4
Steel tank + appurtenances dead load, W_tank (kips) |  | 40
Concrete foundation self-weight will be computed |  | 0
Snow + roof live load (kips) |  | 13.4648
Wind overturning moment at base (kip-ft) |  | 34.3242
Seismic base shear (kips) |  | 108.4665
Load combinations |  | 975.7589

## Geometry
Foundation Geometry
Ringwall / Ring Footing Geometry (circular)
Ringwall thickness (ft) | 1.6667
Footing base width, B (ft) | 3.0833
Radius to foundation centerline, R_cl (ft) | 9
Top of concrete elevation (ft) | 1274.5
Footing edge thickness (ft) | 1.1667
Concrete cover to rebar (in) | 3
Derived Dimensions
Inner radius to footing edge, R_in (ft) | 7.4583
Outer radius to footing edge, R_out (ft) | 10.5417
Footing plan area, A (ft^2) | 174.3584
Ringwall centerline radius (ft) (if needed) | 9.8333

## Bearing & Stability
Soil Bearing, Uplift, and Stability Checks
Service-Level Bearing Pressure
Inputs
Water weight, Ww (kips) | 83.4167
Tank dead load, W(tank) (kips) | 40
Superimposed (snow/live/wind) (kips) | 13.4648 | Enter as needed
Footing self-weight, W_f (kips) | 30.5127 | teq = edge thickness; adjust if needed
Total service vertical load, V_s (kips) | 167.3942
Allowable bearing, q_allow (ksf) | 4
Results
Service bearing pressure, qs = V_s/A (ksf) | 0.96006
Bearing utilization, qs/q_allow | 0.24001 | OK if <= 1.0

## Flexure (Ring Footing)
Flexural Design (per 1-ft circumferential strip)
Inputs
Factored moment demand, Mu (kip-in/ft) | 12 |  | Enter from analysis (soil pressure, uplift, etc.) Here I used for the normal ringwall foundition.
Effective depth, d (in) | 11 |  | Uses edge thickness and cover
Strip width, b (in) | 12
Concrete strength, f'c (psi) | 4000
Steel yield, fy (psi) | 60000
Steel modulus, Es (psi) | 29000000
Lightweight factor, λ | 1
Design Calculations (per ACI 318-19 Ch.21–22)
β1 (Table 22.2.2.4.3) | 0.85 |  | Mu must be provided
Yield strain, εty = fy/Es (21.2.2.1) | 0.002069
As provided (in²/ft) (from bar selection) | 0.79 |  | if we use Bar #8
a = As*fy / (0.85 f'c b) (in) (22.2.2.4.1) | 1.1618 |  | Check per member type
c = a/β1 (in) (22.2.2.4.1) | 1.3668
Net tensile strain, εt = 0.003*(d-c)/c (22.2.2.1) | 0.021144
0.9
Mn = As*fy*(d-a/2) (lb-in/ft) | 493866.1765
ϕMn (kip-in/ft) | 444.4796 |  | Options: No.4, No.5, No.6
Utilization = Mu / (ϕMn) | 0.026998
Required spacing s (in) for As provided | 0.23703 |  | Spacing = Ab*12/As
Reference: As required assuming ϕ = 0.90 (tension-controlled)
Mn_req = Mu/ϕ (lb-in/ft) | 13333.3333
As_req (in²/ft) (steel yields) | 0.020229
Bar Selection Helper
Select bar size | No.6
Bar area Ab (in²) | 0.44
Provide spacing s (in) | 5 | Assumption
As provided = Ab*(12/s) (in²/ft) | 1.056
Spacing for As_req (in) = Ab*12/As_req | 261.0066

## Shear Checks (legacy) (hidden)
One-Way & Two-Way (Punching) Shear Checks (Generic)
Inputs
Factored shear demand Vu (kips) |  | Enter from analysis
Effective depth d (in) | 11
Concrete strength f'c (psi) | 4000
Phi for shear, ϕ | 0.75
One-way shear width b (in) | 12 | Per 1-ft strip
Punching perimeter bo (in) |  | Enter perimeter at d/2 from load area
One-Way Shear (ACI 318-19)
Vc = 2*sqrt(f'c)*b*d (lb) | 16696.826
ϕVc (kips) | 12.5226
Utilization Vu/(ϕVc)
Punching Shear (ACI 318-19)
Vcp = 4*sqrt(f'c)*bo*d (lb) (interior column baseline)
ϕVcp (kips)
Utilization Vu/(ϕVcp)

## Shear & Bearing (ACI 21-22)
Shear & Bearing Checks (ACI 318-19 Ch. 21–22)
Inputs
Concrete strength, f'c (psi) | 4000 | psi
Lightweight factor, λ (Table 19.2.4.1) | 1
Shear strength reduction factor, ϕv (Table 21.2.1) | 0.75
Bearing strength reduction factor, ϕb (Table 21.2.1) | 0.65
Effective depth, d (in) | 11 | in
Strip width, b_w (in) (use 12 in for per-foot strip) | 12 | in
As provided for strip (in²/ft) (from flexure sheet) | 0.79 | in²/ft | x
Member overall thickness, h (in) | 14 | in
Derived terms
Size effect factor, λs = min(1, 2/(1 + d/10)) (Eq. 22.5.5.1.3) | 0.95238
Reinforcement ratio, ρw = As/(b_w*d) | 0.0059848
Gross area for strip, Ag = bw*h | 168 | in²
One-Way Shear (22.5) — No shear reinforcement (use Table 22.5.5.1(c))
Factored one-way shear demand, Vu (kips/ft) |  | kips/ft
Axial load Nu on strip (kips) (compression +, tension −) (Table 22.5.5.1 note) | 0 | kips
Vc (lb/ft) = [8·λs·λ·ρw^(1/3)·√f'c + Nu/(6Ag)] · b_w · d (Table 22.5.5.1(c)) |  | lb/ft
ϕ·Vc (kips/ft) |  | kips/ft
Utilization = Vu / (ϕ·Vc)
Two-Way (Punching) Shear (22.6) — No shear reinforcement (Table 22.6.5.2)
Factored punching shear demand, Vu,p (kips) |  | kips
Critical perimeter, b0 (in) at d/2 from loaded area (22.6.4.1) |  | in
β = long/short side ratio of loaded area (Table 22.6.5.2 note) | 1
Column / load location (Interior / Edge / Corner) (22.6.5.3) | Interior
αs (22.6.5.3) = 40 interior, 30 edge, 20 corner | 40
vc(a) = 4·λs·λ·√f'c (Table 22.6.5.2(a)) |  | psi
vc(b) = (2 + 4/β)·λs·λ·√f'c (Table 22.6.5.2(b)) |  | psi
vc(c) = (2 + αs·d/b0)·λs·λ·√f'c (Table 22.6.5.2(c)) |  | psi
vc = least of (a),(b),(c) (Table 22.6.5.2) |  | psi
Vc,p (lb) = vc·b0·d |  | lb
ϕ·Vc,p (kips) |  | kips
Utilization = Vu,p / (ϕ·Vc,p)
Bearing (22.8) — Concrete bearing strength
Factored compressive force through bearing, Bu (kips) |  | kips
Loaded area, A1 (in²) |  | in²
Supporting area, A2 (in²) (lower base of 1V:2H frustum) (22.8.3.2) |  | in²
Supporting surface wider on all sides than loaded area? (Yes/No) | Yes
Bn (lb) per Table 22.8.3.2 |  | lb
ϕ·Bn (kips) |  | kips
Utilization = Bu / (ϕ·Bn)

## Summary
Design Summary
Geometry (as-designed defaults)
Ringwall thickness (ft) | 1.6667
Footing width B (ft) | 3.0833
Foundation centerline radius R_cl (ft) | 9
Plan area A (ft^2) | 174.3584
Service bearing q_s (ksf) | 0.96006
Bearing utilization | 0.24001
Flexure As provided (in²/ft) | 0.79
Flexure utilization Mu/(ϕMn) | 0.026998
Provided bar spacing s (in) | 5
One-way shear utilization Vu/(ϕVc)
Punching shear utilization Vu,p/(ϕVc,p)
ACI concrete bearing utilization Bu/(ϕBn)

## Thank Information
Volumn (Gal.) | Diameter (ft) | Centroied (ft) | tank height (ft) | Weight of water (Kips) | Weight of steel (Kips) | Total weight (Kips) | projected area (ft2)
50K-DE | 24 | 11.5 | 23.001 | 421 | 25.0264 | 446.0264 | 470
100K-DE | 32 | 12.6 | 25.2156 | 879 | 40.3865 | 919.3865 | 612
200K-DE | 38 | 16 | 31.5884 | 1729 | 63.6953 | 1792.6953 | 982
250K-TORO | 43 | 14.1 | 29.6777 | 2139 | 69.913 | 2208.913 | 1067
300K-TORO | 43 | 16 | 34.5944 | 2581 | 84.741 | 2665.741 | 1278
400K-TORO | 50 | 15.8 | 34.3946 | 3353 | 83.7002 | 3436.7002 | 1437
500K-TORO | 56 | 15 | 34.8552 | 4199 | 133.145 | 4332.145 | 1617